{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":55,"n_cols":13,"rows_kept":55,"merged":[[0,0,0,12],[1,0,1,12],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,11,4,11],[2,12,4,12]],"flags":["formulas_cached_only"]}
["02上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2026.02.02","淄博市政务中心","20260202-0101",4,"未检出","<5","0.20","无",0.06,"/","2026.02.04"," 王晓芳"]
[2,"2026.02.02","车站街道办事处","20260202-0102",2,"未检出","<5","0.21","无",0.05,"/","2026.02.04"," 王晓芳"]
[3,"2026.02.02","王舍生活二区","20260202-0103",1,"未检出","<5","0.23","无",0.04,1.29,"2026.02.04"," 王晓芳"]
[4,"2026.02.02","石家社区","20260202-0104",5,"未检出","<5","0.24","无",0.04,"/","2026.02.04"," 王晓芳"]
[5,"2026.02.02","福源汇社区","20260202-0105",7,"未检出","<5","0.20","无",0.05,"/","2026.02.04"," 王晓芳"]
[6,"2026.02.02","通济花园社区","20260202-0106",10,"未检出","<5","0.26","无",0.03,"/","2026.02.04"," 王晓芳"]
[7,"2026.02.03","淄博市委","20260203-0107",5,"未检出","<5","0.31","无",0.05,"/","2026.02.05"," 王晓芳"]
[8,"2026.02.03","五里桥生活区","20260203-0108",3,"未检出","<5","0.24","无",0.04,"/","2026.02.05"," 王晓芳"]
[9,"2026.02.03","于小社区","20260203-0109",6,"未检出","<5","0.26","无",0.04,"/","2026.02.05"," 王晓芳"]
[10,"2026.02.03","碧桂园社区","20260203-0110",2,"未检出","<5","0.28","无",0.05,"/","2026.02.05"," 王晓芳"]
[11,"2026.02.03","孝妇河湿地公园","20260203-0111",7,"未检出","<5","0.26","无",0.03,1.53,"2026.02.05"," 王晓芳"]
[12,"2026.02.03","福瑞家园社区","20260203-0112",9,"未检出","<5","0.19","无",0.04,1.45,"2026.02.05"," 王晓芳"]
[13,"2026.02.03","盛世康城社区","20260203-0113",13,"未检出","<5","0.21","无",0.04,"/","2026.02.05"," 王晓芳"]
[14,"2026.02.04","黄金国际社区","20260204-0114",7,"未检出","<5","0.29","无",0.05,"/","2026.02.06"," 王晓芳"]
[15,"2026.02.04","市自来水公司新区营业所","20260204-0115",3,"未检出","<5","0.24","无",0.05,"/","2026.02.06"," 王晓芳"]
[16,"2026.02.04","颐丰花园社区","20260204-0116",5,"未检出","<5","0.31","无",0.04,"/","2026.02.06"," 王晓芳"]
[17,"2026.02.04","世纪花园社区","20260204-0117",8,"未检出","<5","0.30","无",0.04,1.42,"2026.02.06"," 王晓芳"]
[18,"2026.02.04","瑞丰苑社区","20260204-0118","未检出","未检出","<5","0.27","无",0.05,"/","2026.02.06"," 王晓芳"]
[19,"2026.02.04","科技苑社区","20260204-0119",11,"未检出","<5","0.21","无",0.03,"/","2026.02.06"," 王晓芳"]
[20,"2026.02.05","山泉路70号","20260205-0120",3,"未检出","<5","0.20","无",0.05,"/","2026.02.07"," 王晓芳"]
[21,"2026.02.05","四砂社区","20260205-0121",15,"未检出","<5","0.29","无",0.03,1.33,"2026.02.07"," 王晓芳"]
[22,"2026.02.05","经开区后南定村","20260205-0122",5,"未检出","<5","0.25","无",0.05,"/","2026.02.07"," 王晓芳"]
[23,"2026.02.05","苹果园社区","20260205-0123",17,"未检出","<5","0.35","无",0.06,{"v":1.3,"d":"1.30"},"2026.02.07"," 王晓芳"]
[24,"2026.02.05","五公里社区","20260205-0124",9,"未检出","<5","0.22","无",0.04,"/","2026.02.07"," 王晓芳"]
[25,"2026.02.05","张南路101号","20260205-0125",2,"未检出","<5",{"v":0.2,"d":"0.20"},"无",0.04,"/","2026.02.07"," 王晓芳"]
[26,"2026.02.06","北苑社区","20260206-0126",5,"未检出","<5","0.32","无",0.04,"/","2026.02.08"," 王晓芳"]
[27,"2026.02.06","金都花园社区","20260206-0127",2,"未检出","<5","0.20","无",0.04,1.47,"2026.02.08"," 王晓芳"]
[28,"2026.02.06","丁庄社区","20260206-0128",4,"未检出","<5","0.21","无",0.06,"/","2026.02.08"," 王晓芳"]
[29,"2026.02.06","外商居住区","20260206-0129",1,"未检出","<5","0.19","无",0.04,"/","2026.02.08"," 王晓芳"]
[30,"2026.02.06","华侨城社区","20260206-0130",20,"未检出","<5","0.35","无",0.03,"/","2026.02.08"," 王晓芳"]
[31,"2026.02.06","高新区高科技创业园","20260206-0131",13,"未检出","<5","0.20","无",0.04,"/","2026.02.08"," 王晓芳"]
[32,"2026.02.09","淄博市自来水公司宿舍区","20260209-0132",1,"未检出","<5","0.19","无",0.06,"/","2026.02.11"," 王晓芳"]
[33,"2026.02.09","行政执法局湖田中队","20260209-0133",5,"未检出","<5","0.28","无",0.03,"/","2026.02.11"," 王晓芳"]
[34,"2026.02.09","洪三社区","20260209-0134",9,"未检出","<5","0.25","无",0.04,"/","2026.02.11"," 王晓芳"]
[35,"2026.02.09","西张社区","20260209-0135",6,"未检出","<5","0.33","无",0.06,1.35,"2026.02.11"," 王晓芳"]
[36,"2026.02.09","恒嘉园社区","20260209-0136",2,"未检出","<5","0.31","无",0.04,"/","2026.02.11"," 王晓芳"]
[37,"2026.02.09","金乔社区","20260209-0137",4,"未检出","<5","0.21","无",0.07,1.33,"2026.02.11"," 王晓芳"]
[38,"2026.02.09","潘庄社区","20260209-0138",4,"未检出","<5","0.20","无",0.06,"/","2026.02.11"," 王晓芳"]
[39,"2026.02.10","四宝山街道办事处","20260210-0139",3,"未检出","<5","0.23","无",0.06,"/","2026.02.12"," 王晓芳"]
[40,"2026.02.10","淄博市十一中","20260210-0140",7,"未检出","<5","0.19","无",0.05,"/","2026.02.12"," 王晓芳"]
[41,"2026.02.10","大张社区","20260210-0141",5,"未检出","<5","0.22","无",0.04,1.32,"2026.02.12"," 王晓芳"]
[42,"2026.02.10","齐悦国际社区","20260210-0142",2,"未检出","<5","0.29","无",0.03,"/","2026.02.12"," 王晓芳"]
[43,"2026.02.10","凯瑞溪园社区","20260210-0143",4,"未检出","<5","0.23","无",0.06,"/","2026.02.12"," 王晓芳"]
[44,"2026.02.11","北西五路5号院","20260211-0144",6,"未检出","<5","0.34","无",0.05,"/","2026.02.13"," 王晓芳"]
[45,"2026.02.11","祥瑞花园社区","20260211-0145",8,"未检出","<5","0.25","无",0.04,"/","2026.02.13"," 王晓芳"]
[46,"2026.02.11","张店八中","20260211-0146",5,"未检出","<5","0.23","无",0.04,"/","2026.02.13"," 王晓芳"]
[47,"2026.02.11","积家村社区","20260211-0147",16,"未检出","<5","0.31","无",0.05,1.37,"2026.02.13"," 王晓芳"]
[48,"2026.02.11","明德苑社区","20260211-0148",2,"未检出","<5","0.20","无",0.03,1.29,"2026.02.13"," 王晓芳"]
[49,"2026.02.11","花漾城社区","20260211-0149",3,"未检出","<5","0.28","无",0.05,"/","2026.02.13"," 王晓芳"]
[50,"2026.02.11","淄博市档案馆","20260211-0150",7,"未检出","<5","0.23","无",0.03,"/","2026.02.13"," 王晓芳"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}