{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":55,"n_cols":13,"rows_kept":55,"merged":[[0,0,0,12],[1,0,1,12],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,11,4,11],[2,12,4,12]],"flags":["formulas_cached_only"]}
["02下半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2026.02.12","淄博市政务中心","20260212-0151",3,"未检出","<5","0.22","无",0.05,"/","2026.02.14"," 王晓芳"]
[2,"2026.02.12","车站街道办事处","20260212-0152",10,"未检出","<5","0.25","无",0.04,"/","2026.02.14"," 王晓芳"]
[3,"2026.02.12","王舍生活二区","20260212-0153",7,"未检出","<5","0.25","无",0.05,1.45,"2026.02.14"," 王晓芳"]
[4,"2026.02.12","石家社区","20260212-0154",9,"未检出","<5","0.26","无",0.05,"/","2026.02.14"," 王晓芳"]
[5,"2026.02.12","福源汇社区","20260212-0155",11,"未检出","<5","0.23","无",0.04,"/","2026.02.14"," 王晓芳"]
[6,"2026.02.12","通济花园社区","20260212-0156",6,"未检出","<5","0.27","无",0.04,"/","2026.02.14"," 王晓芳"]
[7,"2026.02.13","淄博市委","20260213-0157",12,"未检出","<5","0.32","无",0.06,"/","2026.02.15"," 王晓芳"]
[8,"2026.02.13","五里桥生活区","20260213-0158",9,"未检出","<5","0.26","无",0.05,"/","2026.02.15"," 王晓芳"]
[9,"2026.02.13","于小社区","20260213-0159",5,"未检出","<5","0.24","无",0.05,"/","2026.02.15"," 王晓芳"]
[10,"2026.02.13","碧桂园社区","20260213-0160",8,"未检出","<5","0.27","无",0.04,"/","2026.02.15"," 王晓芳"]
[11,"2026.02.13","孝妇河湿地公园","20260213-0161",11,"未检出","<5","0.28","无",0.04,1.67,"2026.02.15"," 王晓芳"]
[12,"2026.02.13","福瑞家园社区","20260213-0162",6,"未检出","<5","0.21","无",0.03,1.56,"2026.02.15"," 王晓芳"]
[13,"2026.02.13","盛世康城社区","20260213-0163",10,"未检出","<5","0.23","无",0.04,"/","2026.02.15"," 王晓芳"]
[14,"2026.02.14","黄金国际社区","20260214-0164",9,"未检出","<5","0.31","无",0.05,"/","2026.02.16"," 王晓芳"]
[15,"2026.02.14","市自来水公司新区营业所","20260214-0165",11,"未检出","<5","0.26","无",0.05,"/","2026.02.16"," 王晓芳"]
[16,"2026.02.14","颐丰花园社区","20260214-0166",7,"未检出","<5","0.28","无",0.04,"/","2026.02.16"," 王晓芳"]
[17,"2026.02.14","世纪花园社区","20260214-0167",13,"未检出","<5","0.32","无",0.05,1.72,"2026.02.16"," 王晓芳"]
[18,"2026.02.14","瑞丰苑社区","20260214-0168",2,"未检出","<5","0.29","无",0.03,"/","2026.02.16"," 王晓芳"]
[19,"2026.02.14","科技苑社区","20260214-0169",8,"未检出","<5","0.24","无",0.04,"/","2026.02.16"," 王晓芳"]
[20,"2026.02.24","山泉路70号","20260224-0170",2,"未检出","<5","0.22","无",0.06,"/","2026.02.26"," 王晓芳"]
[21,"2026.02.24","四砂社区","20260224-0171",11,"未检出","<5","0.31","无",0.04,1.69,"2026.02.26"," 王晓芳"]
[22,"2026.02.24","经开区后南定村","20260224-0172","未检出","未检出","<5","0.26","无",0.05,"/","2026.02.26"," 王晓芳"]
[23,"2026.02.24","苹果园社区","20260224-0173",9,"未检出","<5","0.36","无",0.05,1.59,"2026.02.26"," 王晓芳"]
[24,"2026.02.24","五公里社区","20260224-0174",15,"未检出","<5","0.24","无",0.05,"/","2026.02.26"," 王晓芳"]
[25,"2026.02.24","张南路101号","20260224-0175",4,"未检出","<5",0.22,"无",0.06,"/","2026.02.26"," 王晓芳"]
[26,"2026.02.25","北苑社区","20260225-0176",7,"未检出","<5","0.34","无",0.03,"/","2026.02.27"," 王晓芳"]
[27,"2026.02.25","金都花园社区","20260225-0177",4,"未检出","<5","0.22","无",0.05,1.79,"2026.02.27"," 王晓芳"]
[28,"2026.02.25","丁庄社区","20260225-0178",6,"未检出","<5","0.23","无",0.04,"/","2026.02.27"," 王晓芳"]
[29,"2026.02.25","外商居住区","20260225-0179",3,"未检出","<5","0.20","无",0.03,"/","2026.02.27"," 王晓芳"]
[30,"2026.02.25","华侨城社区","20260225-0180",15,"未检出","<5","0.36","无",0.04,"/","2026.02.27"," 王晓芳"]
[31,"2026.02.25","高新区高科技创业园","20260225-0181",9,"未检出","<5","0.19","无",0.03,"/","2026.02.27"," 王晓芳"]
[32,"2026.02.26","淄博市自来水公司宿舍区","20260226-0182",5,"未检出","<5","0.22","无",0.06,"/","2026.02.28"," 王晓芳"]
[33,"2026.02.26","行政执法局湖田中队","20260226-0183",8,"未检出","<5","0.30","无",0.04,"/","2026.02.28"," 王晓芳"]
[34,"2026.02.26","洪三社区","20260226-0184",11,"未检出","<5","0.24","无",0.03,"/","2026.02.28"," 王晓芳"]
[35,"2026.02.26","西张社区","20260226-0185",3,"未检出","<5","0.31","无",0.05,1.57,"2026.02.28"," 王晓芳"]
[36,"2026.02.26","恒嘉园社区","20260226-0186",4,"未检出","<5","0.33","无",0.05,"/","2026.02.28"," 王晓芳"]
[37,"2026.02.26","金乔社区","20260226-0187",2,"未检出","<5","0.22","无",0.05,1.53,"2026.02.28"," 王晓芳"]
[38,"2026.02.26","潘庄社区","20260226-0188",6,"未检出","<5","0.19","无",0.06,"/","2026.02.28"," 王晓芳"]
[39,"2026.02.27","四宝山街道办事处","20260227-0189",5,"未检出","<5","0.21","无",0.05,"/","2026.03.01"," 王晓芳"]
[40,"2026.02.27","淄博市十一中","20260227-0190",3,"未检出","<5","0.23","无",0.04,"/","2026.03.01"," 王晓芳"]
[41,"2026.02.27","大张社区","20260227-0191",8,"未检出","<5","0.24","无",0.05,1.62,"2026.03.01"," 王晓芳"]
[42,"2026.02.27","齐悦国际社区","20260227-0192",6,"未检出","<5","0.31","无",0.03,"/","2026.03.01"," 王晓芳"]
[43,"2026.02.27","凯瑞溪园社区","20260227-0193",9,"未检出","<5","0.25","无",0.05,"/","2026.03.01"," 王晓芳"]
[44,"2026.02.28","北西五路5号院","20260228-0194",3,"未检出","<5","0.36","无",0.06,"/","2026.03.02"," 王晓芳"]
[45,"2026.02.28","祥瑞花园社区","20260228-0195",2,"未检出","<5","0.27","无",0.05,"/","2026.03.02"," 王晓芳"]
[46,"2026.02.28","张店八中","20260228-0196",9,"未检出","<5","0.25","无",0.04,"/","2026.03.02"," 王晓芳"]
[47,"2026.02.28","积家村社区","20260228-0197",11,"未检出","<5","0.33","无",0.04,1.65,"2026.03.02"," 王晓芳"]
[48,"2026.02.28","明德苑社区","20260228-0198",7,"未检出","<5","0.21","无",0.04,1.73,"2026.03.02"," 王晓芳"]
[49,"2026.02.28","花漾城社区","20260228-0199",5,"未检出","<5","0.29","无",0.06,"/","2026.03.02"," 王晓芳"]
[50,"2026.02.28","淄博市档案馆","20260228-0200",9,"未检出","<5","0.24","无",0.04,"/","2026.03.02"," 王晓芳"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}